SUPREMA SECURE MULTI-DOOR I/O MODULE - DM-20

TECHNICAL SPECIFICATIONS

2024-02-13

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the DM-20.

SUMMARY

A door control module, capable of configuring and controlling multiple doors by connecting Wiegand readers and various I/O devices.

REFERENCE

- Standards

Conformity for Europe (CE)

UK Conformity Assessed (UKCA)

Korea Certification (KC)

FCC - Code of Federal Regulations, Title 47, Part 15, Class B

Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: Door Module

- Part Number: DM-20

Alternates: NONE

DESCRIPTION

- The door control module controls Wiegand readers and various I/O devices.

- Capable of controlling up to 62 Wiegand readers when connected as daisy-chain via RS-485.

- Provides various Interfaces.

- RS-485, TTL Input/Output, Wiegand, Relay, Supervised Input.

FEATURES

- Door control with multiple inputs and outputs.

- Control the connected Wiegand reader’s LED, Buzzer, Tamper, and more.

- Detect 4 states such as ON, OFF, Open and Short with 4ch Supervised Inputs.

- RS-485, TTL Input/Output, Wiegand, Relay, Supervised Input.

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | CPU | Cortex M3 72 MHz |
|  | Memory | 128 KB Flash, 20 KB SRAM |
|  | LED | Multi-color - Power x 1 - Relay x 4 - TTL Input x 4 - Supervised Input x 4 - TTL Output x 6 - RS-485 x 2 - Run x 1 |
|  | Operating Temperature | -20 °C ~ 60 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 80 %, non-condensing |
|  | Storage Humidity | 0 % ~ 90 %, non-condensing |
|  | Dimension (W x H x D) | 130 x 90.5 x 35.8 (mm) |
|  | Certificates | CE, UKCA, KC, FCC, RoHS, REACH, WEEE |
| Interface | RS-485 | 1 ch |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | TTL Input | 4 ch |
|  | TTL Output | 6 ch |
|  | Supervised Input | 4 ch |
|  | Relay | 4 Relays |
|  | Wiegand | 2 ch Inputs - Voltage: 12 Vdc - Current: Max. 1.5 A |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 3.1 A |
|  | Relay | 2 A @ 30 VDC Resistive load 1 A @ 30 VDC Inductive load |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The device shall be stored in an environment where humidity is in the range of 0 % ~ 90 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20 °C ~ 60 °C.

- The device shall be installed in an environment where humidity is in the range of 0 % ~ 80 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION