SUPREMA DOOR EXPANSION MODULE – Door Interface

TECHNICAL SPECIFICATIONS

2025-04-14

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the Door Interface.

SUMMARY

A door expansion module, capable of configuring and controlling multiple doors by connecting readers and various devices.

REFERENCE

- Standards

- FCC - Code of Federal Regulations, Part 15, Class A

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- UK Conformity Assessed (UKCA)

- Korea Certification (KC)

- Regulatory Compliance Mark (RCM)

- Industry Canada (IC)

- Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

- The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: Door Interface

- Part Number: DI-24

Alternates: NONE

DESCRIPTION

- The Door Interface is a door expansion module that allows easy configuration of up to two doors.

      - Capable of controlling up to 64 readers when connected as daisy-chain via RS-485.

- Offline operation mode for Uninterrupted Security.

- Provides various Interfaces.

      - RS-485 (OSDP), Wiegand, Supervised Input, and AUX.

FEATURES

- Offline facility code mode

- Green LED/Red LED/Buzzer control

- Dedicated Fire, Tamper, Power Fail inputs

- OSDP V2 compliant

- Built-in RS-485 terminations

- Sensors, locks, alarm devices
- RS-485(OSDP), Wiegand, Relay, Input, Output, Supervised Input, Aux

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | Model | DI-24 |
|  | CPU | 1.2 GHz Single Core |
|  | Memory | 4 GB Flash + 256 MB RAM |
|  | Crypto Chip | Supported |
|  | LED | - POWER: RED single-color - STATUS: Multi-color |
|  | Operating Temperature | 0 °C ~ 50 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 80 %, non-condensing |
|  | Storage Humidity | 0 % ~ 95 %, non-condensing |
|  | Operational Ambient Conditions | 0 °C ~ 49 °C |
|  | Dimension (W x H x D) | 100 x 190 x 33.9 (mm) |
|  | Weight | 279 g |
|  | Certificates | CE, UKCA, KC, FCC, RCM, IC, RoHS, REACH, WEEE, EAC |
| Capacity | Max. Text Log | 400 |
| Interface | RS-485 | 3 ch |
|  | RS-485 Communication Protocol | OSDP V2 Compliant |
|  | Wiegand | 2 ch |
|  | Relay | 4 relays |
|  | Input | 6 ch1) |
|  | Output | 6 ch |
|  | Supervised Input | 6 ch1) |
|  | AUX Input | 3 ch (AC POWER FAIL, Tamper, Fire) |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 2.8 A |
|  |  | - Voltage: 24 Vdc - Current: Max. 1.4 A |
|  | Power Output | 12 Vdc - Reader: Max. 0.6 A (0.3 A x 2) - Lock: Max. 1.2 A (0.6 A x 2) |
|  |  | 24 Vdc - Reader: Max. 0.3 A (0.15 A x 2) - Lock: Max. 0.6 A (0.3 A x 2) |
|  | Switch Input VIH | - Max.: 5 V - Min.: 3 V |
|  | Switch Input VIL | Max.: 1 V |
|  | Relay | 5 A @ 30 VDC Resistive load |
| Platform | BioStar 2 | Supported |

1) Input or Supervised Input selectable.

- Product specifications are subject to change without notice to improve.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The controller shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The controller shall be stored in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

INSTALLATION

- The controller shall be installed in an environment where temperature is in the range of 0 °C ~ 49 °C.

- The controller shall be installed in an environment where humidity is in the range of 0 % ~ 80 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION