SUPREMA SECURE MULTI-OUTPUT MODULE - OM-120

TECHNICAL SPECIFICATIONS

2024-02-14

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the OM-120.

SUMMARY

A multi-output module, capable of connected to Biometric/RFID devices to control access to zones or floors.

REFERENCE

- Standards

FCC - Code of Federal Regulations, Part 15, Class A

Conformity for Europe (CE)

UK Conformity Assessed (UKCA)

Korea Certification (KC)

Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: Output Module

- Part Number: OM-120

Alternates: NONE

DESCRIPTION

- The multi-output module, capable of configuring and controlling zones or floors with BioStar 2.

- Support 12 relay outputs per module.

FEATURES

- Control up to 192 floors per elevator with BioStar 2 when connected as daisy chains via RS-485.

- Capable of setting the floor access privilege in BioStar 2 when connected Biometric/RFID devices.

- Switchable on-board RS-485 termination.

- Interlock with Anti-passback zones and Fire Alarm zones, manage to occur specific outputs when an alarm is triggered.

- RS-485, AUX Input, Relay.

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | CPU | Cortex M3 72 MHz |
|  | Memory | 128 KB Flash, 20 KB SRAM |
|  | LED | Multi-color - POWER - 1 - RELAY - 12 - RS-485 TX - 1 - RS-485 RX - 1 - AUX IN - 2 - STATUS - 1 |
|  | Operating Temperature | -20 °C ~ 60 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 95 %, non-condensing |
|  | Storage Humidity | 0 % ~ 95 %, non-condensing |
|  | Dimension (W x H x D) | 90 x 190 x 21 (mm) |
|  | Weight | 300 g |
|  | Certificates | CE, UKCA, KC, FCC, RoHS, REACH, WEEE |
| Interface | RS-485 | 1 ch |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | AUX Input | 2 ch Dry Contact Input |
|  | Relay | 12 Relays |
| Capacity | Text Log | 10 ea per port |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 0.6 A |
|  | Switch Input VIH | Max. 5 V (Dry Contact) |
|  | Relay | 5 A @ 30 VDC Resistive load |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The device shall be stored in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20 °C ~ 60 °C.

- The device shall be installed in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION