SUPREMA ACCESS CONTROL DEVICE - Secure I/O 2

TECHNICAL SPECIFICATIONS

2024-02-15

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the Secure I/O 2.

SUMMARY

Section includes a RF reader and door controller with RS-485 connectivity.

Product - An I/O expanding device, capable of connecting with biometric/RF reader via RS-485 and controlling relays and external signal input.

REFERENCE

- Standards

FCC - Code of Federal Regulations, Title 47, Part 15, Class B

Conformity for Europe (CE)

UK Conformity Assessed (UKCA)

Korea Certification (KC)

Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

- Model(s) name: Secure I/O 2

- Part Number: SIO2

Alternates: NONE

DESCRIPTION

- The I/O device shall be an I/O expanding device capable of connecting with biometric/RF reader via RS-485 and controlling relays and external signal input.

FEATURES

- Encrypted communication with connected device

- Compact size

- Easy to installation

Supports 1 relay, 2 external inputs

- RS-485, TTL, Relay interface

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | CPU | Cortex M3 72 MHz |
|  | Memory | 128 KB Flash + 20 KB RAM |
|  | LED | Multi-color - PWR - RS-485 TX/RX - IN1/IN2 - RELAY |
|  | Operating Temperature | -20 °C ~ 50 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 80 %, non-condensing |
|  | Storage Humidity | 0 % ~ 90 %, non-condensing |
|  | Dimension (W x H x D) | 36 x 65 x 18 (mm) |
|  | Weight | - Device: 37 g - Bracket: 1 g |
|  | Certificates | CE, UKCA, KC, FCC, RoHS, REACH, WEEE, ETL Listed to UL 294 |
| Interface | RS-485 | 1 ch |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | TTL Input | 2 ch |
|  | Relay | 1 Relay |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 0.5 A |
|  | Relay | 2 A @ 30 VDC Resistive load 1 A @ 30 VDC Inductive load |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The device shall be stored in an environment where humidity is in the range of 0 % ~ 90 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20 °C ~ 50 °C.

- The device shall be installed in an environment where humidity is in the range of 0 % ~ 80 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION