SUPREMA ACCESS CONTROL DEVICE – X-Station 2

TECHNICAL SPECIFICATIONS

2025-07-23

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the X-Station 2.

SUMMARY

Section includes a biometric reader and door controller with Ethernet network connectivity.

Product—An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints, RFID cards, QR/Barcode, and mobile access cards, managing users, and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Part 15, Class A

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- UK Conformity Assessed (UKCA)

- Korea Certification (KC)

- Industry Canada (IC)

- Regulatory Compliance Mark (RCM)

- Bluetooth SIG

- Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

- The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defects in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: X-Station 2

- Part Number: XS2

- Sub Model

- XS2-ODPB: Optical fingerprint, EM, MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV3, FeliCa, Mobile Access Card (NFC, BLE) supported

- XS2-OAPB: Optical fingerprint, EM, HID Prox, MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV3, FeliCa, iCLASS SE/SR/Seos, Mobile Access Card (NFC, BLE) supported

Alternates: NONE

DESCRIPTION

- The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints, RFID cards, QR/Barcode, and mobile access cards, managing users and controlling access.

FEATURES

- Time Attendance and Access Control device based on Android 9 Pie

- 1.5 GHz Quad Core with 1 GB RAM

- Mobile Access card support (NFC, BLE)

- Multi-class RFID card reading

- IP65, Dust & Waterproof

- 4" IPS color LCD with capacitive touch screen

- TCP/IP, RS-485, Wiegand, Input, Relay, USB, PoE, Tamper

- Intuitive Graphical User Interface (GUI) system

- Enhanced Security and Data Protection

- Expanded Capacity for more users and security logs

- FBI PIV and FBI Mobile ID FAP20 certified

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | RF Option | - XS2-ODPB: 125 kHz EM & 13.56 MHz MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV31), FeliCa |
|  |  | - XS2-OAPB: 125 kHz EM, HID Prox & 13.56 MHz MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV31), FeliCa, iCLASS SE/SR/Seos |
|  | RF Read Range2) | EM/HID Prox/MIFARE/DESFire/HID iCLASS: 50 mm, Felica: 30 mm |
|  | Mobile | Frequency: 13.56 MHz NFC & 2.4 GHz BLE |
|  |  | Certificates: ISO 27001 |
|  |  | Encryption: AES-256 |
|  |  | Compatible devices: iOS 7.0 above, Android 9.0 above |
|  | Scramble Keypad (PIN) | Supported |
|  | QR/Barcode3) | Supported4) |
| General | CPU | 1.5 GHz Quad Core |
|  | Memory | 16 GB Flash + 1 GB RAM |
|  | Crypto Chip | Supported |
|  | Display | 4" IPS color LCD |
|  | Display Resolution | 480 x 800 pixels |
|  | Sound | 24 bit |
|  | Operating Temperature | -20 °C ~ 50 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 80 %, non-condensing |
|  | Storage Humidity | 0 % ~ 90 %, non-condensing |
|  | Camera Type | CMOS 2M pixels |
|  | Camera Resolution | 1600 x 1200 pixels |
|  | Dimension (W x H x D) | 82 x 208.5 x 53 (Bottom) / 25.9 (Top) (mm) |
|  | Weight | - Device: 375 g - Bracket: 86 g (Including washer and bolt) |
|  | IP Rating | IP65 |
|  | Certificates | CE, UKCA, KC, FCC, IC, RCM, BIS, ANATEL, SIG, RoHS, REACH, WEEE |
| Fingerprint | Image Dimension | 300 x 400 pixels |
|  | Resolution | 500 dpi |
|  | Template | SUPREMA / ISO19794-2, ANSI-378 |
|  | Extractor / Matcher | MINEX certified and compliant |
|  | Sensor Certificates | FBI PIV and FBI Mobile ID FAP20 |
|  | Live Fingerprint Detection | Supported (SW-based) |
| Capacity | Max. User | 500,0005) |
|  | Max. Credential (1:N) | Fingerprint: 100,000 |
|  | Max. Credential (1:1) | - Fingerprint: 500,000 - Card: 500,000 - PIN: 500,000 |
|  | Max. Text Log | 5,000,000 |
|  | Max. Image Log | 50,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | Network Protocol | TCP, UDP |
|  | RS-485 | 1 ch Master or Slave (Selectable) |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | Wiegand | 1 ch Input or Output (Selectable) |
|  | Input | 2 ch Inputs |
|  | Relay | 1 Relay |
|  | USB | USB 2.0 (Host) |
|  | PoE | Supported (IEEE 802.3af compliant) |
|  | Tamper | Supported |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 0.8 A |
|  |  | - Voltage: 24 Vdc - Current: Max. 0.5 A |
|  | Switch Input VIH | - Min.: 3 V - Max.: 5 V |
|  | Switch Input VIL | Max.: 1 V |
|  | Switch Pull-up Resistance | 4.7 kΩ (The input pots are pulled up with 4.7 kΩ.) |
|  | Wiegand Output VOH | More than 4.8 V |
|  | Wiegand Output VOL | Less than 0.2 V |
|  | Wiegand Output Pull-up Resistance | Internally pulled up with 1 kΩ |
|  | Relay | 2 A @ 30 VDC Resistive load 1 A @ 30 VDC Inductive load |
| Platform | BioStar 2 | Supported |

1) DESFire EV2/EV3 cards are supported by having backward compatibility of DESFire EV1 cards. CSN and smart card functions are compatible with X-Station 2.

2) RF read range will vary depending on installation environment.

3) Supports QR/Barcodes composed of up to 32 ASCII code strings.

4) Requires a separate license.

5) The number of users registered without having any credential data.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust, or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The device shall be stored in an environment where humidity is in the range of 0 % ~ 90 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20 °C~ 50 °C.

- The device shall be installed in an environment where humidity is in the range of 0 % ~ 80 %, non-condensing.

- All wires shall be run through conduits to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

Keep at least 10 cm distance between the devices when installing multiple devices.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 500 mm |
| - 120 mm | - 400 mm |
| - 150 mm | - 300 mm |

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION