SUPREMA ACCESS CONTROL DEVICE - BioEntry P2

TECHNICAL SPECIFICATIONS

2021-07-15

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the BioEntry P2.

SUMMARY

Section includes a biometric reader and door controller with Ethernet network connectivity.

Product - An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints and RFID cards, managing users and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- CE - Radio Equipment Directive 2014/53/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): BioEntry P2

Alternates: NONE

DESCRIPTION

- The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints and RFID cards, managing users and controlling access.

FEATURES

- Access control and time attendance device

- Multi-class RFID card reading, HID multiCLASS support

- Mobile card reading with NFC technology

- Mullion type form-factor

- NIST MINEX certified and compliant

- OSDP V2 Compliant

- TCP/IP, RS-485, Wiegand, TTL, Relay, Tamper

- Built-in card reader with card options (125kHz EM, HID Prox & 13.56 MHz MIFARE, MIFARE Plus, DESFire/ EV1, FeliCa, iCLASS SE/SR/Seos, NFC)

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | Biometric | Fingerprint |
|  | RF Option | BEP2-OD: 125kHz EM & 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC |
|  |  | BEP2-OA: 125kHz EM, HID Prox & 13.56Mhz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, iCLASS SE/SR/Seos, NFC |
|  | RF read range* | MIFARE/DESFire/EM/HID Prox/iCLASS: 50 mm, FeliCa: 30 mm * RF read range will vary depending on the installation environment. |
| General | CPU | 1.0GHz |
|  | Memory | 8GB Flash + 64MB RAM |
|  | LED | Multi-color |
|  | Sound | Buzzer |
|  | Operating temperature | -20°C ~ 50°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Operating humidity | 0% ~ 80%, non-condensing |
|  | Storage humidity | 0% ~ 90%, non-condensing |
|  | Dimension (W x H x D) | 50 mm x 164 mm x 37.5 mm |
|  | Weight | Device: 162g |
|  |  | Bracket: 39g (Including washer and bolt) |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Fingerprint | Image dimension | 272 x 320 pixels |
|  | Image bit depth | 8bit, 256 grayscale |
|  | Resolution | 500 dpi |
|  | Template | SUPREMA / ISO 19794-2 / ANSI 378 |
|  | Extractor / Matcher | MINEX certified and compliant |
|  | LFD | Supported |
| Capacity | Max. User | 10,000 * The number of users registered without having any credential data |
|  | Max. Credential (1:N) | Fingerprint: 10,000 |
|  | Max. Credential (1:1) | Fingerprint: 10,000 Card: 10,000 PIN: 10,000 |
|  | Max. Text Log | 1,000,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | RS-485 | 1ch Host or Slave (Selectable) |
|  | Wiegand | 1ch Input or Output (Selectable) |
|  | TTL input | 2ch Input |
|  | Relay | 1 Relay |
|  | Tamper | Supported |
| Electrical | Power | Voltage: DC 12V Current: Max. 600 mA |
|  | Switch input VIH | Min. 3V Max. 5V |
|  | Switch input VIL | Max. 1V |
|  | Switch Pull-up resistance | 4.7kΩ (The input ports are pulled up with 4.7kΩ.) |
|  | Wiegand output VOH | More than 4.8V |
|  | Wiegand output VOL | Less than 0.2V |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
|  | Relay | Voltage: Max. 30VDC Current: 1A |
| Platform | BioStar 2 | Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C - 50°C.

- The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 270 mm |
| - 120 mm | - 250 mm |
| - 150 mm | - 170 mm |

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION