SUPREMA ACCESS CONTROL DEVICE - BioEntry R2

TECHNICAL SPECIFICATIONS

2017-11-09

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the BioEntry R2.

SUMMARY

Section includes a biometric reader with RS-485(OSDP).

Product - An OSDP enabled biometric reader, capable of scanning and registering fingerprints and RFID cards.

REFERENCE

- Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- CE - Radio Equipment Directive 2014/53/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): BioEntry R2

Alternates: NONE

DESCRIPTION

- The biometric reader shall be a RS-485(OSDP) enabled device capable of scanning fingerprints and RFID cards.

- The biometric reader can be configured the two type of access control system which is the distributed system and the centralized system.

FEATURES

- Dedicated fingerprint and RFID card reader

- Multi-class RFID card reading

- Mobile card reading with NFC technology

- Mullion type form-factor

- NIST MINEX certified and compliant

- OSDP V2 Compliant

- Built-in card reader with card options (125kHz EM & 13.56 MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC)

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | Biometric | Fingerprint |
|  | RF Option | BER2-OD: 125kHz EM & 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC |
|  | RF read range* | MIFARE/DESFire/EM: 50mm, FeliCa: 30mm * RF read range will vary depending on the installation environment. |
| General | CPU | 1.0GHz |
|  | Memory | 32MB Flash + 32MB RAM |
|  | LED | Multi-color |
|  | Sound | Buzzer |
|  | Operating temperature | -20°C ~ 50°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Operating humidity | 0% ~ 80%, non-condensing |
|  | Storage humidity | 0% ~ 90%, non-condensing |
|  | Dimension (W x H x D) | 50 mm x 164 mm x 37.5 mm |
|  | Weight | Device: 158g |
|  |  | Bracket: 39g (Including washer and bolt) |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Fingerprint | Image dimension | 272 x 320 pixels |
|  | Image bit depth | 8bit, 256 grayscale |
|  | Resolution | 500 dpi |
|  | Template | SUPREMA / ISO 19794-2 / ANSI 378 |
| Interface | RS-485 | 1ch slave (OSDP V2 Compliant) |
|  | Tamper | Supported |
| Electrical | Power | Voltage: DC 12V Current: Max. 600 mA |
| Platform | BioStar 2 | Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C - 50°C.

- The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 250 mm |
| - 120 mm | - 250 mm |
| - 150 mm | - 180 mm |

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION