SUPREMA INTELLIGENT BIOMETRIC CONTROLLER - CoreStation

TECHNICAL SPECIFICATIONS

2021-02-16

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the CoreStation.

SUMMARY

Section includes an intelligent biometric controller with Ethernet network connectivity.

Product - An intelligent door controller which is capable of matching fingerprints and RFID cards, managing users and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- CE - Radio Equipment Directive 2014/53/EU

- UL 294

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com

Model(s): CoreStation

Alternates: NONE

DESCRIPTION

- The intelligent door controller which provides the advantage of a biometric-enabled security over a centralized access control system. This controller provides centralized biometric template management and also versatile interfaces with the completed set of reader technologies including RS-485(OSDP) and Wiegand.

FEATURES

- Full-featured intelligent door controller with fingerprint matching

- High performance matching - Max. 400,000 match/sec

- Store up to 500,000 users, 500,000 RFID cards, and 5,000,000 event logs

- Controls up to 132 access points with DM-20

- Elevator control with OM-120

- OSDP V2 compliant

- Built-in RS-485 terminations

- Multi-port interfaces for fingerprint/RFID readers, sensors, locks, alarm devices
- TCP/IP, RS-485(OSDP), Wiegand, Supervised Input, TTL, Relay, Aux

- Easy Installation and Management with CoreStation SETUP Manager

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | CPU | 1.4GHz Octa Core |
|  | Memory | 8GB Flash + 1GB RAM |
|  | Crypto chip | Supported |
|  | LED | Multi-color |
|  | Operating Temperature | 0°C ~ 50°C |
|  | Storage Temperature | -40°C ~ 70°C |
|  | Operating Humidity | 0% ~ 80%, non-condensing |
|  | Storage Humidity | 0% ~ 90%, non-condensing |
|  | Dimension (W x H x D) | 150 mm x 214 mm x 21 mm |
|  | Weight | 415 g |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE, UL 294 Compliant |
| Capacity | Max. User (1:1) | 500,000 |
|  | Max. User (1:N) | 100,000 |
|  | Max. Template (1:1) | 1,000,000 (Two templates per finger) |
|  | Max. Template (1:N) | 200,000 (Two templates per finger) |
|  | Max. Face User (1:1) | 30,000 |
|  | Max. Face User (1:N) | 4,000 |
|  | Max. Card | 500,000 |
|  | Max. PIN | 500,000 |
|  | Max. Text Log | 5,000,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | RS-485 | 5 ch |
|  | RS-485 Communication Protocol | OSDP V2 Compliant |
|  | Wiegand | 4 ch |
|  | Relay | 4 relays |
|  | Supervised Input | 8 ch (TTL input selectable) |
|  | TTL Output | 8 ch |
|  | AUX Input | 2 ch (AC POWER FAIL, TAMPER) |
| Electrical | Power | CoreStation - Voltage: 12 VDC, Current: Max. 3A Power Supply (SMPS) AC INPUT - 110 ~ 240 VAC, 50/60 Hz |
|  | Power Output | Voltage: 12 VDC Current: Max. 1.5A * Shared power output. |
|  | Switch input VIH | Max.: 5 V Min.: 3 V |
|  | Switch input VIL | Max. 1V |
|  | Relay | 5 A @ 30 VDC Resistive load |
| Platform | BioStar 2 | Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The controller shall be stored in an environment where temperature is in the range of -40°C-70°C.

- The controller shall be stored in an environment where humidity is in the range of 0%-90%, non-condensing.

INSTALLATION

- The controller shall be installed in an environment where temperature is in the range of 0°C-50°C.

- The controller shall be installed in an environment where humidity is in the range of 0%-80%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION