SUPREMA SECURE MULTI-DOOR I/O MODULE - DM-20

TECHNICAL SPECIFICATIONS

2018-07-10

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the DM-20.

SUMMARY

A door control module, capable of configuring and controlling multiple doors by connecting Wiegand readers and various I/O devices.

REFERENCE

- Standards

FCC - Code of Federal Regulations, Title 47, Part 15, Class B

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): DM-20

Alternates: NONE

DESCRIPTION

- The door control module controls Wiegand readers and various I/O devices.

- Capable of controlling up to 62 Wiegand readers when connected as daisy-chain via RS-485.

- Provides various Interfaces.

- RS-485, TTL Input/Output, Wiegand, Relay, Supervised Input.

FEATURES

- Door control with multiple inputs and outputs.

- Control the connected Wiegand reader’s LED, Buzzer, Tamper, and more.

- Detect 4 states such as ON, OFF, Open and Short with 4ch Supervised Inputs.

- RS-485, TTL Input/Output, Wiegand, Relay, Supervised Input.

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | CPU | Cortex M 32Mhz |
|  | Memory | Flash 128KB, SRAM 20KB |
|  | LED | Multi-color - Power 1ea - Relay 4 ea - TTL Input 4 ea - Supervised Input 4ea - TTL Output 6ea - RS-485 2ea - Run 1ea |
|  | Operating temperature | -20°C ~ 60°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Storage humidity | 0% ~ 90%, non-condensing |
|  | Dimension (W x H x D) | 130 mm x 90.5 mm x 35.8 mm |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Interface | RS-485 | 1ch |
|  | Wiegand | 2ch |
|  | Input | TTL Input x 4 Supervised Input x 4 |
|  | Output | TTL Output x 6 |
|  | Relay | 4 Relays |
| Electrical | Power | Voltage: 12 VDC Current: Max. 2.5A |
|  | Relay | Rated load: 0.4 A @ 125 VAC, 2 A @ 30 VDC Maximum switching voltage: 250 VAC, 220 VDC Maximum switching current: 3 A |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C - 60°C.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION