SUPREMA ACCESS CONTROL DEVICE – X-Station 2

TECHNICAL SPECIFICATIONS

2021-09-27

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the X-Station 2.

SUMMARY

Section includes an RF&QR/barcode reader and door controller with Ethernet network connectivity.

Product—An IP enabled RF&QR/barcode reader and door controller, capable of scanning and registering RFID cards, and mobile access cards, managing users, and controlling access.

REFERENCE

- Standards

- IEEE 802.3af Ethernet Standards

- FCC - Code of Federal Regulations, Part 15, Class A

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- Korea Certification (KC)

- Registration, Evaluation, Authorization, and Restriction of Chemicals (REACH)—EC No. 1907/2006

- The Waste Electrical and Electronic Equipment (WEEE)—Directive 2012/19/EU

- ANSI/IEC60529—Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC)—Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defects in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com

Model(s) name: X-Station 2

- Part Number: XS2

- Sub Model

- XS2-QDPB: QR/barcode, EM, MIFARE, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

- XS2-QAPB: QR/barcode, EM, MIFARE, iCLASS, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

- XS2-DPB: EM, MIFARE, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

- XS2-APB: EM, MIFARE, iCLASS, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

Alternates: NONE

DESCRIPTION

- The RF & QR/barcode reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning RFID cards, and mobile access cards, managing users and controlling access.

FEATURES

- Time Attendance and Access Control device based on Android 9 Pie

- 1.5 GHz Quad Core with 1 GB RAM

- Multiple credential options of RFID cards, Mobile Access and QR/barcodes

- Multi-class RFID card reading

- IP65, Dust & Waterproof

- 4" IPS color LCD with capacitive touch screen

- TCP/IP, RS-485, Wiegand, TTL, Relay, USB, Tamper

- Intuitive Graphical User Interface (GUI) system

- Enhanced Security and Data Protection

- Expanded Capacity for more users and security logs

SPECIFICATIONS

| Category | Feature | Specification |  |
| --- | --- | --- | --- |
| Credential | RF Option | - XS2-DPB, XS2-QDPB: 125 kHz EM & 13.56 MHz MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV3*, FeliCa - XS2-APB, XS2-QAPB: 125 kHz EM, HID Prox & 13.56 MHz MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV3*, FeliCa, iCLASS SE/SR/Seos |  |
|  | RF read range | MIFARE, DESFire, iCLASS, HID Prox, EM: 50 mm/ Felica: 30 mm * RF read range will vary depending on the installation environment. |  |
|  | Mobile | Frequency: 13.56 MHz NFC & 2.4 GHz BLE |  |
|  |  | Certificates: ISO 27001 |  |
|  |  | Encryption: AES-256 |  |
|  |  | Compatible devices: iOS 7.0 above, Android 9.0 above |  |
|  | QR/Barcode | Supported (XS2-QDPB, XS2-QAPB) |  |
|  | QR/Barcode decode ranges | 5 mil Code 39 | Near: 2.0 inch/5.1 cm Far: 6.4 inch/16.2 cm |
|  |  | 5 mil Code 128 | Near: 2.5 inch/6.3 cm Far: 5.0 inch/12.7 cm |
|  |  | 6.6 mil PDF417 | Near: 2.5 inch/6.3 cm Far: 6.3 inch/16.0 cm |
|  |  | 10 mil PDF417 | Near: 1.8 inch/4.5 cm* Far: 9.0 inch/22.8 cm |
|  |  | 13 mil 100% UPC | Near: 2.0 inch/5.0 cm* Far: 12.5 inch/31.7 cm |
|  |  | 20 mil Code 39 | Near: 2.0 inch/5.0 cm* Far: 19.5 inch/49.5 cm |
|  |  | 20 mil Data Matrix | Near: 1.5 inch/3.8 cm Far: 13.5 inch/34.3 cm |
|  |  | 20 mil QR Code | Near: 1.5 inch/3.8 cm Far: 11.0 inch/27.9 cm |
|  | QR/Barcode regulatory | LED Classifications | Exempt Risk Group LED product per IEC/EN 62471 |
|  |  | Electrical Safety | Complies with IEC/EN 60950-1 + A1 + A2 and UL 60950-1-07, 2nd Edition, 2014-10 |
|  | Scramble keypad (PIN) | Supported |  |
| General | CPU | 1.5 GHz Quad Core |  |
|  | Memory | 16 GB Flash + 1 GB RAM |  |
|  | Crypto chip | Supported |  |
|  | LCD type | 4" IPS color LCD |  |
|  | LCD resolution | 480 x 800 pixels |  |
|  | Sound | 24 bit |  |
|  | Operating temperature | -20°C–50°C |  |
|  | Storage temperature | -40°C–70°C |  |
|  | Operating humidity | 0 %–80 %, non-condensing |  |
|  | Storage humidity | 0 %–90 %, non-condensing |  |
|  | Camera type | CMOS 2M pixels |  |
|  | Camera resolution | 1600 x 1200 |  |
|  | Dimension (W x H x D) | XS2-DPB, XS2-APB: 82 x 159 x 25.9 (mm) XS2-QDPB, XS2-QAPB: 82 x 203 x 33.9 (mm) |  |
|  | Weight | Device XS2-DPB, XS2-APB: 280 g XS2-QDPB, XS2-QAPB: 343 g |  |
|  |  | Bracket (Including washer and bolt) XS2-DPB, XS2-APB: 67 g (Including washer and bolt) XS2-QDPB, XS2-QAPB: 88 g (Including washer and bolt) |  |
|  | Certificates | KC, CE, FCC (Compliance: RoHS, REACH, WEEE) |  |
| Capacity | Max. User | 500,000 |  |
|  | Max. Card | 500,000 |  |
|  | Max. Text Log | 5,000,000 |  |
|  | Max. Image Log | 50,000 |  |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |  |
|  | RS-485 | 1 ch Host or Slave (Selectable) |  |
|  | Wiegand | 1 ch Input or Output (Selectable) |  |
|  | TTL input | 2 ch Inputs |  |
|  | Relay | 1 Relay |  |
|  | PoE | Supported (IEEE 802.3af compliant) |  |
|  | USB | USB 2.0 (Host) |  |
|  | Tamper | Supported |  |
| Electrical | Power | DC 12 V (Max. 0.8 A) or DC 24 V (Max. 0.45 A) |  |
|  | Switch input VIH | Min. 3 V Max. 5 V |  |
|  | Switch input VIL | Max. 1 V |  |
|  | Switch Pull-up resistance | 4.7 kΩ (The input pots are pulled up with 4.7 kΩ.) |  |
|  | Wiegand output VOH | More than 4.8 V |  |
|  | Wiegand output VOL | Less than 0.2 V |  |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |  |
|  | Relay | Voltage: Max. 30 VDC Current: Max. 1 A |  |
| Platform | BioStar 2 | Supported |  |

* DESFire EV2/EV3 cards are supported by having backward compatibility of DESFire EV1 cards. CSN and smart card functions are compatible with X-Station 2.

* Limited by the width of barcode in the field of view

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust, or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C–+70°C.

- The device shall be stored in an environment where humidity is in the range of 0%–90%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C–50°C.

- The device shall be installed in an environment where humidity is in the range of 0%–80%, non-condensing.

- All wires shall be run through conduits to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

Keep at least 10 cm distance between the devices when install multiple devices

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 500 mm |
| - 120 mm | - 400 mm |
| - 150 mm | - 300 mm |

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION