SUPREMA ACCESS CONTROL DEVICE – X-Station 2

TECHNICAL SPECIFICATIONS

2021-11-15

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the X-Station 2.

SUMMARY

Section includes a biometric reader and door controller with Ethernet network connectivity.

Product—An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints, RFID cards, mobile access cards, managing users, and controlling access.

REFERENCE

- Standards

- IEEE 802.3af Ethernet Standards

- FCC—Code of Federal Regulations, Part 15, Class A

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- Korea Certification (KC)

- Registration, Evaluation, Authorization, and Restriction of Chemicals (REACH)—EC No. 1907/2006

- The Waste Electrical and Electronic Equipment (WEEE)—Directive 2012/19/EU

- ANSI/IEC60529—Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC)—Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defects in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com

Model(s) name: X-Station 2

- Part Number: XS2

- Sub Model

- XS2-ODPB: Optical fingerprint, EM, MIFARE, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

- XS2-OAPB: Optical fingerprint, EM, MIFARE, iCLASS, FeliCa multi-frequency, Mobile Card (NFC, BLE) supported

Alternates: NONE

DESCRIPTION

- The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints, RFID cards, and mobile access cards, managing users and controlling access.

FEATURES

- Time Attendance and Access Control device based on Android 9 Pie

- 1.5 GHz Quad Core with 1 GB RAM

- Mobile Access card support (NFC, BLE)

- Multi-class RFID card reading

- IP65, Dust & Waterproof

- 4" IPS color LCD with capacitive touch screen

- TCP/IP, RS-485, Wiegand, TTL, Relay, USB, Tamper

- Intuitive Graphical User Interface (GUI) system

- Enhanced Security and Data Protection

- Expanded Capacity for more users and security logs

- FBI PIV and FBI Mobile ID FAP20 certified

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | RF Option | - XS2-ODPB: 125 kHz EM & 13.56 MHz MIFARE, MIFARE Plus, DESFire EV1/EV2*, FeliCa - XS2-OAPB: 125 kHz EM, HID Prox & 13.56 MHz MIFARE, MIFARE Plus, DESFire EV1/EV2*, FeliCa, iCLASS SE/SR/Seos |
|  | RF read range | MIFARE, DESFire, iCLASS, HID Prox, EM: 50 mm/ Felica: 30 mm * RF read range will vary depending on the installation environment. |
|  | Fingerprint | Image dimension: 300 x 400 pixels |
|  |  | Resolution: 500 dpi |
|  |  | Template: SUPREMA/ISO 19794-2/ANSI 378 |
|  |  | Extractor/Matcher: MINEX certified and compliant |
|  |  | Sensor Certificates: FBI PIV and FBI Mobile ID FAP20 |
|  |  | Live Fingerprint Detection: Supported (SW-based) |
|  | Mobile | Frequency: 13.56 MHz NFC & 2.4 GHz BLE |
|  |  | Certificates: ISO 27001 |
|  |  | Encryption: AES-256 |
|  |  | Compatible devices: iOS 7.0 above, Android 9.0 above |
|  | Scramble keypad (PIN) | Supported |
| General | CPU | 1.5 GHz Quad Core |
|  | Memory | 16 GB Flash + 1 GB RAM |
|  | Crypto chip | Supported |
|  | LCD type | 4" IPS color LCD |
|  | LCD resolution | 480 x 800 pixels |
|  | Sound | 24 bit |
|  | Operating temperature | -20°C–50°C |
|  | Storage temperature | -40°C–70°C |
|  | Operating humidity | 0 %–80 %, non-condensing |
|  | Storage humidity | 0 %–90 %, non-condensing |
|  | Camera type | CMOS 2M pixels |
|  | Camera resolution | 1600 x 1200 |
|  | Dimension (W x H x D) | 82 mm x 208.5 mm x 25.9(53) mm |
|  | Weight | Device: 375 g |
|  |  | Bracket (Including washer and bolt): 86 g |
|  | Certificates | KC, CE, FCC (Compliance: RoHS, REACH, WEEE) |
| Capacity | Max. User | 500,000** |
|  | Max. Credential (1:N) | Fingerprint: 100,000 |
|  | Max. Credential (1:1) | - Fingerprint: 500,000 - Card: 500,000 - PIN: 500,000 |
|  | Max. Text Log | 5,000,000 |
|  | Max. Image Log | 50,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | RS-485 | 1 ch Host or Slave (Selectable) |
|  | Wiegand | 1 ch Input or Output (Selectable) |
|  | TTL input | 2 ch Inputs |
|  | Relay | 1 Relay |
|  | PoE | Supported (IEEE 802.3af compliant) |
|  | USB | USB 2.0 (Host) |
|  | Tamper | Supported |
| Electrical | Power | - Power: DC 12 V (Max. 0.8 A) or DC 24 V (Max. 0.45 A) - Adapter recommended specifications: DC 12 V (± 10%) with a minimum of 1,500 mA or DC 24 V (±10%) with a minimum of 800 mA*** |
|  | Switch input VIH | Min. 3 V Max. 5 V |
|  | Switch input VIL | Max. 1 V |
|  | Switch Pull-up resistance | 4.7 kΩ (The input pots are pulled up with 4.7 kΩ.) |
|  | Wiegand output VOH | More than 4.8 V |
|  | Wiegand output VOL | Less than 0.2 V |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
|  | Relay | 2 A @ 30 VDC Resistive load 1 A @ 30 VDC Inductive load |
| Platform | BioStar 2 | Supported |

* These documents must be kept completely confidential.

* DESFire EV2 cards are supported by having backward compatibility of DESFire EV1 cards. CSN and smart card functions are compatible with X-Station 2.

** The number of users registered without any credential data

*** Adapter is sold separately. Refer to the recommended specifications.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust, or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C–70°C.

- The device shall be stored in an environment where humidity is in the range of 0 %–90 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20°C–50°C.

- The device shall be installed in an environment where humidity is in the range of 0 %–80 %, non-condensing.

- All wires shall be run through conduits to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

Keep at least 10 cm distance between the devices when installing multiple devices

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 500 mm |
| - 120 mm | - 400 mm |
| - 150 mm | - 300 mm |

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION