SUPREMA OUTDOOR COMPACT RFID DEVICE – XPass 2(XP2-MDPB)

TECHNICAL SPECIFICATIONS

2021-06-29

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the XPass 2(XP2-MDPB).

SUMMARY

Section includes a RFID device with Ethernet network connectivity.

An IP enabled RF device, capable of scanning and registering RFID cards.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- Conformity for Europe (CE) - R&TTE Directive 1999/5/EC

- Korea Certification (KC)

- Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP67

- IEC 62262 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts IK08

- The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

- Bluetooth SIG

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support.supremainc.com

Model(s): XPass 2(XP2-MDPB)

Alternates: NONE

DESCRIPTION

- The RF device which is an IP enabled device capable of scanning RFID cards and mobile cards.

FEATURES

- Multi-RFID card reading

- Mobile card support (NFC, BLE)

- IP65, IP67, Dust & Waterproof

- IK08, Vandal proof

- Mullion type design

- TCP/IP, RS-485, Wiegand, Tamper

- OSDP V2 Compliant

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
|  |  | XP2-MDPB |
| Credential | LF card option | EM |
|  | HF card option | MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV3, FeliCa |
|  | NFC card | Supported |
|  | BLE card | Supported |
|  | RF read range* | MIFARE/DESFire/EM : 50 mm, FeliCa: 30 mm * RF read range will vary depending on the installation environment. |
| General | CPU | 1 GHz |
|  | Memory | 4 GB Flash + 64 MB RAM |
|  | LED | Multi-color |
|  | Sound | Multi-tone Buzzer |
|  | Operating temperature | -35°C ~ 65°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Operating humidity | 0% ~ 95%, non-condensing |
|  | Storage humidity | 0% ~ 95%, non-condensing |
|  | Dimension (W x H x D) | 48 mm x 145 mm x 27 mm |
|  | Weight | Device: 144g |
|  |  | Bracket: 30g (Including washer and bolt) |
|  | IP rating | IP65, IP67 |
|  | IK rating | IK08 |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE, SIG |
| Capacity | Max. User | 200,000 |
|  | Max. Card | 200,000 |
|  | Max. Text Log | 1,000,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | RS-485 | 1ch Master or Slave (Selectable) |
|  | Wiegand | 1ch Input or Output (Selectable) |
|  | TTL Input | 2ch Input |
|  | Relay | 1 Relay |
|  | PoE | Supported (IEEE 802.3af compliant) |
|  | Tamper | Supported |
| Electrical | Power | Voltage: DC 12 V, Current: Max. 500 mA or Voltage: DC 24 V, Current: Max. 250 mA * Use 12 VDC, 1 A / 24 VDC, 0.5 A power supply |
|  | Switch input VIH | Min. 3V Max. 5V |
|  | Switch input VIL | Max. 1V |
|  | Switch Pull-up resistance | 4.7kΩ (The input ports are pulled up with 4.7kΩ.) |
|  | Wiegand output VOH | More than 4.8V |
|  | Wiegand output VOL | Less than 0.2V |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
|  | Relay | Voltage: Max. 30 VDC Current: Max. 2 A |
| Platform | BioStar 2 | Supported |
|  | BioStar 1 | Not Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

- IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 95%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -35°C - 65°C.

- The device shall be installed in an environment where humidity is in the range of 0% - 95%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 360 mm |
| - 120 mm | - 360 mm |
| - 150 mm | - 300 mm |

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION