SUPREMA OUTDOOR COMPACT RFID READER – XPass D2(XPD2-GDB)

TECHNICAL SPECIFICATIONS

2018-07-04

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the XPass D2(XPD2-GDB).

SUMMARY

An OSDP enabled RF reader, capable of scanning and registering RFID cards.

REFERENCE

- Standards

- FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP67

- IEC 62262 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts IK08

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): XPass D2(XPD2-GDB)

Alternates: NONE

DESCRIPTION

- The RF reader which is an RS-485(OSDP) enabled device capable of scanning RFID cards and mobile cards.

FEATURES

- Multi-RFID card reading

- Mobile card support (NFC, BLE)

- IP65, IP67, Dust & Water Proof

- IK08, Vandal proof

- Gangbox type design

- RS-485, Wiegand, Tamper

- OSDP V2 Compliant

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
|  |  | XPD2-GDB |
| Credential | LF card option | EM |
|  | HF card option | MIFARE, MIFARE Plus, DESFire/EV1, FeliCa |
|  | NFC card | Supported |
|  | BLE card | Supported |
|  | RF read range* | MIFARE/DESFire/EM : 50 mm, FeliCa: 30 mm * RF read range will vary depending on the installation environment. |
| General | CPU | 80 MHz |
|  | Memory | 256 KB Flash + 64 KB RAM |
|  | LED | Multi-color |
|  | Sound | Multi-tone Buzzer |
|  | Operating temperature | -35°C ~ 65°C |
|  | Storage temperature | -40°C ~ 70°C |
|  | Operating humidity | 0% ~ 95%, non-condensing |
|  | Storage humidity | 0% ~ 95%, non-condensing |
|  | Dimension (W x H x D) | 80 mm x 130 mm x 25 mm |
|  | Weight | Device: 140 g |
|  |  | Bracket: 52 g (Including washer and bolt) |
|  | IP rating | IP65, IP67 |
|  | IK rating | IK08 |
|  | Certificates | CE, FCC, KC, RoHS, REACH, WEEE, SIG |
| Interface | RS-485 | 1ch |
|  | Wiegand | 1ch |
|  | LED | 2ch |
|  | Beep | 1ch |
|  | Tamper | Supported |
| Electrical | Power | Voltage: DC 12 V, Current: Max. 400 mA |
|  | Switch input VIH | Min. 3V Max. 5V |
|  | Switch input VIL | Max. 1V |
|  | Switch Pull-up resistance | 4.7kΩ (The input ports are pulled up with 4.7kΩ.) |
|  | Wiegand output VOH | More than 4.8V |
|  | Wiegand output VOL | Less than 0.2V |
|  | Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
| Platform | BioStar 2 | Supported |
|  | BioStar 1 | Not Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.

- The device shall be stored in an environment where humidity is in the range of 0% - 95%, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -35°C - 65°C.

- The device shall be installed in an environment where humidity is in the range of 0% - 95%, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 400 mm |
| - 120 mm | - 380 mm |
| - 150 mm | - 380 mm |

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION