SUPREMA ACCESS CONTROL DEVICE - Xpass S2

TECHNICAL SPECIFICATIONS

2017-06-05

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the Xpass S2.

SUMMARY

Section includes a RF reader and door controller with Ethernet network connectivity.

Product - An IP enabled RF reader and door controller, capable of scanning and registering cards, managing users and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

FCC - Code of Federal Regulations, Title 47, Part 15, Class B

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, www.supremainc.com
support@supremainc.com

Model(s): Xpass S2

Alternates: NONE

DESCRIPTION

- The RF reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning RFID cards, managing users and controlling access.

FEATURES

- 11.4 mm super slim design

Supports up to 50,000 users and 100,000 logs

IP65 certified

Operates between -35 °C to 65 °C

- TCP/IP, RS-485, Wiegand, Relay interface

- Multi smartcard reading (13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa)

SPECIFICATIONS

| General | IP Rating | IP65 |
| --- | --- | --- |
|  | RF Option | XPS2M: 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1 (CSN), FeliCa |
|  | Multi-Controller | Yes |
|  | Certificates | CE, FCC, KC, RoHS, REACH |
| Capacity | Max. User (1:1) | 50,000 |
|  | Max. User (1:N) | 50,000 |
|  | Max. Text Log | 100,000 |
| Interface | TCP/IP | Yes |
|  | RS-485 | 1ch Host or 1ch Slave (Selectable) |
|  | Wiegand | 1ch In or 1ch Out (Selectable) |
|  | Input | 2 Inputs |
|  | Relay | 1 Relay |
| Mechanical | CPU | 533MHz DSP |
|  | Memory | 16MB RAM + 16MB Flash |
|  | LED Indicator | Multi-Color |
|  | Sound | Multi-tone Buzzer |
|  | Operating Temp. | -35° to 65°C |
|  | Tamper | Yes |
|  | Dimensions | 80 x 120 x 11.4 (WxHxD mm) |
| Electrical | Power | Min. 10 VDC Typ. 12 VDC Max. 13 VDC |
|  | Consumption | Max. 270 mA |
|  | Switch Input VIN | Max. 5.0 V |
|  | Relay | Form C Relay Voltage: Max. 24 VDC Current: Typ. 0.5 A, Max. 1 A |
| Platform | BioStar 1 | Supported |
|  | BioStar 2 | Supported |

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The system shall be stored in an environment where temperature is in the range of -95 - 149°F (-35 - +65°C).

INSTALLATION

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION