SUPREMA QR/Barcode and RFID reader – XPass Q2

TECHNICAL SPECIFICATIONS

2026-04-06

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the XPass Q2.

SUMMARY

Section includes a QR/Barcode and RFID reader with Ethernet network connectivity.

An IP enabled device capable of scanning and registering RFID cards, QR/Barcodes, and mobile access cards.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- UK Conformity Assessed (UKCA)

- Korea Certification (KC)

- FCC - Code of Federal Regulations, Part 15, Class A

- Industry Canada (IC)

- Regulatory Compliance Mark (RCM)

- Bluetooth SIG

- Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

- The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

- Telecom Engineering Center (TELEC)

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: XPass Q2

- Part Number: XPQ2

Alternates: NONE

DESCRIPTION

- The RF device is an IP-enabled device capable of scanning RFID cards, QR/Barcodes, and mobile access cards.

FEATURES

- Mobile access card support (NFC, BLE)

- Multi-class RFID card reading

- IP65, Dust & Waterproof

- TCP/IP, RS-485, Wiegand, Input, Relay, USB, Extended USB, Tamper

- OSDP V2 Compliant

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credential | RF Option | 125kHz EM & 13.56MHz MIFARE, MIFARE Plus, DESFire, DESFire EV1/EV2/EV31), FeliCa |
|  | RF Read Range2) | EM/MIFARE/DESFire: 50 mm, FeliCa: 30 mm |
|  | Mobile | NFC, BLE |
|  | QR/Barcode3) | Supported4) |
| General | CPU | 1.0 GHz |
|  | Memory | 8 GB Flash + 256 MB RAM |
|  | Crypto Chip | Supported |
|  | LED | Multi-color |
|  | Sound | Multi-tone Buzzer |
|  | Operating Temperature | -20 °C ~ 60 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 95 %, non-condensing |
|  | Storage Humidity | 0 % ~ 95 %, non-condensing |
|  | Camera | 1 Camera (QR only) |
|  | Dimension (W x H x D) | - Device: 50 x 150 x 40.2 (mm) - Bracket: 41.7 x 140.6 (mm) |
|  | Weight | - Device: 213 g - Bracket: 40 g (Including washer and bolt) |
|  | IP Rating | IP65 |
|  | Authentication | CE, UKCA, KC, FCC, IC, RCM, SIG, RoHS, REACH, WEEE, EAC, TELEC |
| Capacity | Max. User | 200,0005) |
|  | Max. Credentials (1:N) | Card: 200,000 |
|  | Max. Credentials (1:1) | Card: 200,000 |
|  | Max. Text Log | 1,000,000 |
| Interface | Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
|  | Network Protocol | TCP, UDP |
|  | RS-485 | 1 ch Master / Slave (Selectable) |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | Wiegand | 1 ch Input / 1 ch Output (Selectable) |
|  | Input | 3 ch Inputs |
|  | Relay | 1 relay |
|  | USB | USB 2.0 (Type C), only FW-Upgrade |
|  | USB Expansion Port | Supported |
|  | Tamper | Supported |
| Electrical | Power | 12 Vdc - DC OUT not used Current: Max. 0.5 A - DC OUT used Current: Max. 2.6 A 24 Vdc - DC OUT not used Current: Max. 0.3 A - DC OUT used Current: Max. 1.4 A |
|  | Power Output | 12 Vdc - Reader: Max. 0.5 A - Lock: Max. 1.2 A 24 Vdc - Reader: Max. 0.25 A - Lock: Max. 0.6 A |
|  | Switch Input VIH | - Min.: 3 V - Max.: 5 V |
|  | Switch Input VIL | Max.: 1 V |
|  | Switch Pull-up Resistance | 4.7 kΩ (The input ports are pulled up with 4.7 kΩ.) |
|  | Wiegand Output VOH | More than 4.8 V |
|  | Wiegand Output VOL | Less than 0.2 V |
|  | Wiegand Output Pull-up Resistance | Internally pulled up with 1 kΩ |
|  | Relay | 2 A @ 30 VDC Resistive load 1 A @ 30 VDC Inductive load |
| Platform | BioStar X | Supported |
|  | BioStar 2 | Supported |
|  | BioStar 1 | Not Supported |

1) DESFire EV2/EV3 cards are backward compatible with DESFire EV1 cards, supporting CSN and smart card features, including those of the DESFire EV1 card.

2) RF read range will vary depending on installation environment.

3) Supports QR codes with up to 32 ASCII characters.

4) Camera QR license is required to use more diverse QR/barcode authentication. For more information on device licenses, refer to the BioStar X Administrator Guide.

- Barcode types supported by the Camera QR license: QR Code, DataMatrix, Aztec, Micro QR Code, PDF417, Code39, Code128, UPC-A, UPC-E, EAN-8, EAN-13

5) Based on users registered without credentials.

- Product specifications are subject to change without notice for performance improvement.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

- IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The device shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The device shall be stored in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

INSTALLATION

- The device shall be installed in an environment where temperature is in the range of -20 °C ~ 60 °C.

- The device shall be installed in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

To avoid RF interference, a minimum separation distance must be maintained.

| - Wall thickness | - Distance |
| --- | --- |
| - 100 mm | - 270 mm |
| - 120 mm | - 250 mm |
| - 150 mm | - 170 mm |

EXAMINATION

- All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION