**SUPREMA ACCESS CONTROL DEVICE - BioLite Solo**

**TECHNICAL SPECIFICATIONS**

2017-06-05

# PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the BioLite Solo.

* 1. SUMMARY
1. Section includes a biometric reader and door controller.
2. Product - A biometric reader and door controller, managing users and controlling access.
	1. REFERENCE
3. Standards
4. FCC - Code of Federal Regulations, Title 47, Part 15, Class B
5. ANSI / IEC60529 – Degrees of Protection Provided by Enclosures
6. International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65
	1. SUBMITTALS
	2. QUALIFICATIONS
7. Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.
8. Installers shall be trained by the Manufacturer to install, configure and commission the access control system.
	1. WARRANTY
9. Manufacturer shall provide a limited ( ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

# PART 2 - PRODUCTS

1. EQUIPMENT
2. Manufacturer
Suprema Inc.
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, [www.supremainc.com](http://www.supremainc.com)
support@supremainc.com
3. Model(s): BioLite Solo
4. Alternates: NONE
5. DESCRIPTION
6. The biometric reader and door controller (“reader/controller”) shall be a device capable of scanning fingerprints, managing users and controlling access.
7. FEATURES
8. NIST MINEX compliant
9. IP65, Dust & Water Proof
10. Standalone biometric access control terminal
11. RS-485, Wiegand, Relay interface
12. SPECIFICATIONS

|  |  |  |
| --- | --- | --- |
| General | Biometric | Fingerprint |
| IP Rating | IP65 |
| Multi-Controller | Yes |
| Certificates | CE, FCC, KC, RoHS |
| Capacity | Max. User (1:1) | 200 |
| Max. User (1:N) | 200 |
| Max. Template (1:1) | 800  |
| Max. Template (1:N) | 800  |
| Max. Text Log | 5,000 |
| Interface | RS-485 | To Slave Only |
| Input | 2 Inputs |
| Relay | 1 Relay |
| Mechanical | CPU | 533MHz DSP |
| Memory | 8MB RAM + 8MB Flash |
| LCD | 128x64 Graphic LCD (Monochrome) |
| LED Indicator | Multi-Color |
| Sound | Multi-tone Buzzer |
| Operating Temp. | -20° to 50°C |
| Tamper | Yes |
| Dimensions | 60 x 185 x 40 (WxHxD mm) |
| Electrical | Power | Min. 10.8 VDCTyp. 12 VDCMax. 13.2 VDC |
| Consumption | Max. 300 mA |
| Switch Input VIH | Min. 2.0 VMax. 10.0 V |
| Switch Input VIL | Max. 0.4 V |
| Switch Pull-up Resistor | 4.7 kΩ (The input ports are pulled up with 4.7 kΩ resistors.) |
| Relay  | Form C Relay Voltage: Max. 24 VDCCurrent: Typ. 0.5 A, Max. 1 A |
| Platform | BioStar 1 | Supported |

END OF SECTION

# PART 3 - EXECUTION

1. INSTALLER
2. Contractor personnel shall comply with all applicable state and local licensing requirements.
3. PREPARATION
4. Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.
5. IP addressing shall be coordinated with the Owner’s responsible IT personnel.
6. STORAGE
7. The system shall be stored in an environment where temperature is in the range of -4 - 122°F (-20 - +50°C).
8. INSTALLATION
9. All wires shall be run through conduit to prevent failure caused by rodent damage.
10. Connections between card readers and a door controller shall not exceed 100 meters.
11. All peripheral devices shall be grounded.
12. EXAMINATION
13. All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION