SUPREMA CENTRALIZED ACCESS CONTROL SYSTEM – CoreStation 20

TECHNICAL SPECIFICATIONS

2025-04-14

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the CoreStation 20.

SUMMARY

Section includes an intelligent door controller with Ethernet network connectivity.

Product - An intelligent door controller which is capable of matching RFID cards, managing users and controlling access.

REFERENCE

- Standards

- IEEE 802.3 Ethernet Standards

- FCC - Code of Federal Regulations, Part 15, Class A

- Conformity for Europe (CE)—Equipment Directive (RED) 2014/53/EU

- UK Conformity Assessed (UKCA)

- Korea Certification (KC)

- Regulatory Compliance Mark (RCM)

- Industry Canada (IC)

- Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

- The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: CoreStation 20

- Part Number: CS-20, CS-20P

Alternates: NONE

DESCRIPTION

- CoreStation 20 is a centralized access control system designed for enterprise environments and can store information for up to 500,000 users.

- Both access control and attendance management can be used through the linkage with BioStar 2, and various interfaces are provided, including RS-485 (OSDP), Wiegand, Supervised input, and AUX.

FEATURES

- Store up to 500,000 users, 500,000 RFID cards, and 5,000,000 event logs

- OSDP V2 compliant

- Built-in RS-485 terminations

- Sensors, locks, alarm devices
- TCP/IP, RS-485(OSDP), Wiegand, Relay, Input, Output, Supervised Input, Aux, PoE+(CS-20P only), SAM Slot(CS-20P only)

- Easy Installation and Management with CoreStation Setup Manager

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| General | Model | CS-20, CS-20P |
|  | CPU | 1.2 GHz Single Core |
|  | Memory | 4 GB Flash + 256 MB RAM |
|  | Crypto Chip | Supported |
|  | LED | - POWER: RED single-color - STATUS: Multi-color |
|  | Operating Temperature | 0 °C ~ 50 °C |
|  | Storage Temperature | -40 °C ~ 70 °C |
|  | Operating Humidity | 0 % ~ 80 %, non-condensing |
|  | Storage Humidity | 0 % ~ 95 %, non-condensing |
|  | Operational Ambient Conditions | 0 °C ~ 49 °C |
|  | Dimension (W x H x D) | 100 x 190 x 33.9 (mm) |
|  | Weight | - CS-20: 285 g - CS-20P: 300 g |
|  | Certificates | CE, UKCA, KC, FCC, RCM, IC, RoHS, REACH, WEEE, EAC |
| Capacity | Max. User | 500,000 |
|  | Max. Credential (1:1) | - Card: 500,000 - PIN: 500,000 |
|  | Max. Text Log | 5,000,000 |
| Interface | Ethernet | Support (10/100 Mbps, Auto MDI/MDI-X) |
|  | RS-485 | 3 ch |
|  | RS-485 Communication Protocol | OSDP V2 Compliant |
|  | Wiegand | 2 ch |
|  | Relay | 4 relays |
|  | Input | 6 ch1) |
|  | Output | 6 ch |
|  | Supervised Input | 6 ch1) |
|  | AUX Input | 3 ch (AC POWER FAIL, Tamper, Fire) |
|  | PoE+ | - CS-20: Not supported - CS-20P: Supported (IEEE 802.3at compliant) |
|  | SAM Slot | - CS-20: Not supported - CS-20P: Supported |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 2.8 A |
|  |  | - Voltage: 24 Vdc - Current: Max. 1.4 A |
|  | Power Output | 12 Vdc - Reader: Max. 0.6 A (0.3 A x 2) - Lock: Max. 1.2 A (0.6 A x 2) |
|  |  | 24 Vdc - Reader: Max. 0.3 A (0.15 A x 2) - Lock: Max. 0.6 A (0.3 A x 2) |
|  |  | PoE+ (12V out) - Reader: Max. 0.6 A (0.3 A x 2) - Lock: Max. 0.6 A (0.6 A x 1) |
|  | Switch Input VIH | - Max.: 5 V - Min.: 3 V |
|  | Switch Input VIL | Max.: 1 V |
|  | Relay | 5 A @ 30 VDC Resistive load |
| Platform | BioStar 2 | Supported |

1) Input or Supervised Input selectable.

- Product specifications are subject to change without notice to improve.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

STORAGE

- The controller shall be stored in an environment where temperature is in the range of -40 °C ~ 70 °C.

- The controller shall be stored in an environment where humidity is in the range of 0 % ~ 95 %, non-condensing.

INSTALLATION

- The controller shall be installed in an environment where temperature is in the range of 0 °C ~ 49 °C.

- The controller shall be installed in an environment where humidity is in the range of 0 % ~ 80 %, non-condensing.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION