SUPREMA ACCESS CONTROL DEVICE - XPass S2

TECHNICAL SPECIFICATIONS

2024-02-22

PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the XPass S2.

SUMMARY

Section includes a RF reader and door controller with Ethernet network connectivity.

Product - An IP enabled RF reader and door controller, capable of scanning and registering cards, managing users and controlling access.

REFERENCE

- Standards

IEEE 802.3 Ethernet Standards

Conformity for Europe (CE)

UK Conformity Assessed (UKCA)

Korea Certification (KC)

FCC - Code of Federal Regulations, Title 47, Part 15, Class B

Registration, Evaluation, Authorization and Restriction of Chemicals (REACH) - (EC No. 1907/2006)

The Waste Electrical and Electronic Equipment (WEEE) - Directive 2012/19/EU

- ANSI / IEC60529 – Degrees of Protection Provided by Enclosures

- International Electrotechnical Commission (IEC) – Ingress Protection Rating IP65

  - SUBMITTALS

QUALIFICATIONS

- Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.

Installers shall be trained by the Manufacturer to install, configure, and commission the access control system.

WARRANTY

- Manufacturer shall provide a limited (  ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

PART 2 - PRODUCTS

EQUIPMENT

- Manufacturer 
Suprema Inc. 
17F Parkview Office Tower, 248, Jeongjail-ro, Seongnam-si, Gyeonggi-do, 13554, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, https://www.supremainc.com
https://support.supremainc.com

Model(s) name: XPass S2

- Part Number: XPS2

Alternates: NONE

DESCRIPTION

- The RF reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning RFID cards, managing users and controlling access.

FEATURES

- 11.4 mm super slim design

Supports up to 50,000 users and 100,000 logs

IP65 certified

Operates between -35 °C to 65 °C

- TCP/IP, RS-485, Wiegand, TTL Input, Relay interface

- Multi smartcard reading (13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa)

SPECIFICATIONS

| Category | Feature | Specification |
| --- | --- | --- |
| Credentials | RF Card | XPS2M: 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1 (CSN), FeliCa, ISO14443A, ISO15693 |
|  | RF Read Range1) | MIFARE/DESFire: 50 mm, FeliCa: 30 mm |
|  | Multi-Controller | Supported |
| General | CPU | 533 MHz DSP |
|  | Memory | 16 MB RAM + 16 MB Flash |
|  | LED | Multi-Color |
|  | Sound | Multi-tone Buzzer |
|  | Operating Temp. | -35 °C ~ 65 °C |
|  | Dimensions (W x H x D) | 80 x 120 x 11.4 (mm) |
|  | IP Rating | IP65 |
|  | Certification | CE, UKCA, KC, FCC, BIS, RoHS, REACH, WEEE |
| Capacity | Max. User (1:1) | 50,000 |
|  | Max. User (1:N) | 50,000 |
|  | Max. Text Log | 100,000 |
| Interface | TCP/IP | Supported |
|  | RS-485 | 1 ch Master / Slave (Selectable) |
|  | RS-485 Communication Protocol | OSDP V2 compliant |
|  | Wiegand | 1 ch Input / Output (Selectable) |
|  | TTL Input | 2 ch |
|  | Relay | 1 Relay - Voltage: Max. 24 Vdc - Current: Typ. 0.5 A, Max. 1.0 A |
|  | Tamper | Supported |
| Electrical | Power | - Voltage: 12 Vdc - Current: Max. 0.4 A |
| Platform | BioStar 1 | Supported |
|  | BioStar 2 | Supported |

1) RF read range will vary depending on installation environment.

END OF SECTION

PART 3 - EXECUTION

INSTALLER

- Contractor personnel shall comply with all applicable state and local licensing requirements.

PREPARATION

- Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.

IP addressing shall be coordinated with the Owner’s responsible IT personnel.

INSTALLATION

- The device shall be stored in an environment where temperature is in the range of -35 °C ~ 65 °C.

- All wires shall be run through conduit to prevent failure caused by rodent damage.

Connections between card readers and a door controller shall not exceed 100 meters.

All peripheral devices shall be grounded.

EXAMINATION

- All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION