**SUPREMA ACCESS CONTROL DEVICE - BioEntry R2**

**TECHNICAL SPECIFICATIONS**

2017-11-09

# PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the BioEntry R2.

* 1. SUMMARY
1. Section includes a biometric reader with RS-485(OSDP).
2. Product - An OSDP enabled biometric reader, capable of scanning and registering fingerprints and RFID cards.
	1. REFERENCE
3. Standards
4. FCC - Code of Federal Regulations, Title 47, Part 15, Class B
5. CE - Radio Equipment Directive 2014/53/EU
	1. SUBMITTALS
	2. QUALIFICATIONS
6. Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.
7. Installers shall be trained by the Manufacturer to install, configure and commission the access control system.
	1. WARRANTY
8. Manufacturer shall provide a limited ( ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

# PART 2 - PRODUCTS

1. EQUIPMENT
2. Manufacturer
Suprema Inc.
17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea
Tel: 82-31-783-4502, Fax: 82-31-783-4503, [www.supremainc.com](http://www.supremainc.com)
support@supremainc.com
3. Model(s): BioEntry R2
4. Alternates: NONE
5. DESCRIPTION
6. The biometric reader shall be a RS-485(OSDP) enabled device capable of scanning fingerprints and RFID cards.
7. The biometric reader can be configured the two type of access control system which is the distributed system and the centralized system.
8. FEATURES
9. Dedicated fingerprint and RFID card reader
10. Multi-class RFID card reading
11. Mobile card reading with NFC technology
12. Mullion type form-factor
13. NIST MINEX certified and compliant
14. OSDP V2 Compliant
15. Built-in card reader with card options (125kHz EM & 13.56 MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC)
16. SPECIFICATIONS

|  |  |  |
| --- | --- | --- |
| **Category** | **Feature** | **Specification** |
| Credential | Biometric | Fingerprint |
| RF Option | **BER2-OD**: 125kHz EM & 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC |
| RF read range\* | MIFARE/DESFire/EM: 50mm, FeliCa: 30mm*\* RF read range will vary depending on the installation environment.* |
| General | CPU | 1.0GHz |
| Memory | 32MB Flash + 32MB RAM |
| LED | Multi-color |
| Sound | Buzzer |
| Operating temperature | -20°C ~ 50°C |
| Storage temperature | -40°C ~ 70°C |
| Operating humidity | 0% ~ 80%, non-condensing |
| Storage humidity | 0% ~ 90%, non-condensing |
| Dimension (W x H x D) | 50 mm x 164 mm x 37.5 mm |
| Weight | Device: 158g |
| Bracket: 39g (Including washer and bolt) |
| Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Fingerprint  | Image dimension | 272 x 320 pixels |
| Image bit depth  | 8bit, 256 grayscale |
| Resolution | 500 dpi |
| Template | SUPREMA / ISO 19794-2 / ANSI 378 |
| Interface | RS-485 | 1ch slave (OSDP V2 Compliant) |
| Tamper | Supported |
| Electrical | Power | Voltage: DC 12V Current: Max. 600 mA |
| Platform | BioStar 2 | Supported |

END OF SECTION

# PART 3 - EXECUTION

1. INSTALLER
2. Contractor personnel shall comply with all applicable state and local licensing requirements.
3. PREPARATION
4. Contractor shall avoid locating the reader in a location subject to direct sunlight, dust or soot.
5. STORAGE
6. The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.
7. The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.
8. INSTALLATION
9. The device shall be installed in an environment where temperature is in the range of -20°C - 50°C.
10. The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.
11. All wires shall be run through conduit to prevent failure caused by rodent damage.
12. Connections between card readers and a door controller shall not exceed 100 meters.
13. All peripheral devices shall be grounded.
14. To avoid RF interference, a minimum separation distance must be maintained.

|  |  |
| --- | --- |
| Wall thickness | Distance |
| 100 mm | 250 mm |
| 120 mm | 250 mm |
| 150 mm | 180 mm |

1. EXAMINATION
2. All connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION