**SUPREMA ACCESS CONTROL DEVICE - BioStation A2**

**TECHNICAL SPECIFICATIONS**

2017-06-05

# PART 1 - GENERAL

The intent of this document is to specify the minimum criteria for the design, supply, installation, and commissioning of the BioStation A2.

* 1. SUMMARY

1. Section includes a biometric reader and door controller with Ethernet network connectivity.
2. Product - An IP enabled biometric reader and door controller, capable of scanning and registering fingerprints and RFID cards, managing users and controlling access.
   1. REFERENCE
3. Standards
4. IEEE 802.3 Ethernet Standards
5. FCC - Code of Federal Regulations, Title 47, Part 15, Class B
   1. SUBMITTALS
   2. QUALIFICATIONS
6. Manufacturer shall be ISO 9001 certified with a minimum of five years’ experience in producing access control equipment.
7. Installers shall be trained by the Manufacturer to install, configure and commission the access control system.
   1. WARRANTY
8. Manufacturer shall provide a limited ( ) month warranty for the product to be free of defect in material and workmanship.

END OF SECTION

# PART 2 - PRODUCTS

1. EQUIPMENT
2. Manufacturer   
   Suprema Inc.   
   17F Parkview Office Tower, Jeongja, Bundang, Seongnam, Gyeonggi, 463-863, Republic of Korea  
   Tel: 82-31-783-4502, Fax: 82-31-783-4503, [www.supremainc.com](http://www.supremainc.com)  
   [support@supremainc.com](mailto:support@supremainc.com)
3. Model(s): BioStation A2
4. Alternates: NONE
5. DESCRIPTION
6. The biometric reader and door controller (“reader/controller”) shall be an IP-enabled device capable of scanning fingerprints and RFID cards, managing users and controlling access.
7. FEATURES
8. Time Attendance and Access Control device based on Android 4.4 KitKat
9. Quad Core 1GHz with 1GB RAM
10. Live Finger Detection (LFD)
11. Built-in Wi-Fi module (IEEE 802.11 b/g)
12. Face detection technology
13. NIST MINEX certified and compliant
14. 5” TFT color LCD with capacitive touch screen
15. CMOS 2M pixels camera
16. Wi-Fi, RS-485, Wiegand, TTL, Relay, USB, SD Card, PoE, Tamper
17. Built-in card reader with card options (125kHz EM, HID Prox. 13.56MHz MIFARE, DESFire/DESFire EV1, FeliCa, iClass SE/SR/Seos, NFC)
18. Intuitive Graphical User Interface (GUI) system
19. SPECIFICATIONS

|  |  |  |
| --- | --- | --- |
| **Category** | **Feature** | **Specification** |
| Credential | Biometric | Fingerprint |
| RF Option | **BSA2-OEPW**: 125kHz EM |
| **BSA2-OHPW**: 125kHz HID Prox |
| **BSA2-OIPW**: 13.56MHz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, iCLASS SE/SR/Seos, NFC |
| **BSA2-OMPW**: 13.56Mhz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, NFC |
| RF read range | MIFARE: 50 mm, DESFire: 50 mm, Felica: 30 mm  *\* RF read range will vary depending on the installation environment.* |
| General | CPU | 1.0 GHz Quad Core |
| Memory | 8GB Flash + 1GB RAM |
| LCD type | 5” color TFT LCD |
| LCD resolution | 480 x 854 pixels |
| LED | Multiple colors |
| Sound | 24 bit/Voice DSP (echo cancel) |
| Operating temperature | -20°C - 50°C |
| Storage temperature | -40°C - 70°C |
| Operating humidity | 0% - 80%, non-condensing |
| Storage humidity | 0% - 90%, non-condensing |
| Camera type | CMOS 2M pixels |
| Camera resolution | 1600 x 1200 pixels |
| Camera angle | Diagonal 122°, Horizontal 64.7°, Vertical 103.3° |
| Dimension (W x H x D) | 155 mm x 155 mm x 40 mm |
| Weight | Device: 440g |
| Bracket: 89g (Including washer and bolt) |
| Certificates | CE, FCC, KC, RoHS, REACH, WEEE |
| Fingerprint | Image dimension | 272 x 320 pixels |
| Image bit depth | 8bit, 256 grayscale |
| Resolution | 500 dpi |
| Template | SUPREMA / ISO 19794-2 / ANSI 378 |
| Extractor / Matcher | MINEX certified and compliant |
| LFD | Supported |
| Capacity | Max. User (1:1) | 500,000 |
| Max. User (1:N) | 100,000 |
| Max. Template (1:1) | 1,000,000 (Two templates per finger) |
| Max. Template (1:N) | 200,000 (Two templates per finger) |
| Max. Text Log | 5,000,000 |
| Max. Image Log | 50,000 |
| Interface | Wi-Fi | Supported (Built-in, IEEE 802.11 b/g) |
| Ethernet | Supported (10/100 Mbps, auto MDI/MDI-X) |
| RS-485 | 1ch Host or Slave (Selectable) |
| Wiegand | 1ch Input, 1ch Output |
| TTL input | 1ch Input |
| Relay | 2 Relay |
| USB | USB 2.0 (Host) |
| SD Card | microSD card (Supports up to 32GB)  *\* The functions of the microSD card are available by customization only.* |
| PoE | Supported (IEEE 802.3af compliant) |
| Tamper | Supported |
| Electrical | Power | Voltage: DC 12V  Current: Max. 850 mA |
| Switch input VIH | Min. 3V Max. 5V |
| Switch input VIL | Max. 1V |
| Switch Pull-up resistance | 4.7kΩ (The input pots are pulled up with 4.7kΩ.) |
| Wiegand output VOH | More than 4.8V |
| Wiegand output VOL | Less than 0.2 V |
| Wiegand output Pull-up resistance | Internally pulled up with 1 kΩ |
| Relay | Voltage: Max. 30VDC Current: Max. 1A |
| Platform | BioStar 2 | Supported |
| BioStar 1 | Supported |

END OF SECTION

# PART 3 - EXECUTION

1. INSTALLER
2. Contractor personnel shall comply with all applicable state and local licensing requirements.
3. PREPARATION
4. Contractor shall avoid locating the reader/controller in a location subject to direct sunlight, dust or soot.
5. IP addressing shall be coordinated with the Owner’s responsible IT personnel.
6. STORAGE
7. The device shall be stored in an environment where temperature is in the range of -40°C - +70°C.
8. The device shall be stored in an environment where humidity is in the range of 0% - 90%, non-condensing.
9. INSTALLATION
10. The device shall be installed in an environment where temperature is in the range of -20°C - 50°C.
11. The device shall be installed in an environment where humidity is in the range of 0% - 80%, non-condensing.
12. All wires shall be run through conduit to prevent failure caused by rodent damage.
13. Connections between card readers and a door controller shall not exceed 100 meters.
14. All peripheral devices shall be grounded.
15. To avoid RF interference, a minimum separation distance must be maintained.

|  |  |
| --- | --- |
| Wall thickness | Distance |
| 100 mm | 500 mm |
| 120 mm | 400 mm |
| 150 mm | 300 mm |

1. EXAMINATION
2. All network connections to the reader/controller shall be tested for proper levels of performance.

END OF SECTION